## Slide 1: Cooling Load Estimation of New SAC Building
Department of Mechanical Engineering
Presented By
Gaurav Kumar (214103327)

## Slide 2: New SAC Building IITG

## Slide 3: Principles modes of heat transfer
Conduction
Convection
Radiation
Design condition
Outdoor design condition:
At peak time, typical Guwahati DBT 98.6 ˚F(37˚C), and 80% RH
Indoor design condition: based upon human comfort
at peak time DBT= 75.2˚F(24˚C), 50% RH

## Slide 4: Space Characteristics
Lightening
Ceiling
Surrounding condition
Window
Occupants
Appliances
Orientation of building
Size of building

## Slide 5: New SAC Building Layout

## Slide 6: Cooling load calculations
Equation used for cooling load temperature difference correction
CLTDC = [CLTD + (78 – TR) +(TM – 85)]
Where
TR= inside design temp=75.2 ˚ F
Daily range= max DBT- min DBT
= 98.6-77 = 21.6F
TM=Mean outdoor temp= Max outdoor temperature-(Daily range/2)
= 98.6-21.6/2 = 87.8˚ F (31˚ C )

## Slide 7: CLTD and CLTDc for different walls
Walls | CLTD | CLTDc
North Wall | 21 | 26.6
South Wall | 26 | 31.6
East Wall | 33 | 38.6

## Slide 8: Calculation of heat transfer coefficient
For North , South and East faced wall
= +
= 0.1799 Btu/hr ft2

## Slide 9: CALCULATION OF HEAT LOAD THROUGH WALLS
Wall | Area(sq.ft) | CLTDc | U(Btu/hr.ft.2 F) | Q(Btu/hr)
North Wall | 2490 | 26.6 | 0.1799 | 11915.5
South Wall | 2490 | 31.6 | 0.1799 | 14155.25
East Wall | 6318 | 38.6 | 0.1799 | 43873.08
Q=U*A*CLTDc

## Slide 10: Calculation of heat transfer coefficient for roof
= + +
= 0.2065 Btu/hr ft^2

## Slide 11: Calculation of for Roof
From ASHRAE fundamentals for 6 inch lightweight concrete
At solar time 4 PM
CLTD = 58
CLTDC = [CLTD + (78 – TR) +(TM – 85)]
= 58 +(78 – 75.2) + (87.8 – 85)
= 63.6

## Slide 12: HEAT LOAD THROUGH GROUND
1/Ug= (L/K) concrete+(L/K)tiles+(1/h)inside air
=(1/0.167)+(0.083/0.147)+(1/3.522)
Ug= 0.152 Btu/hr ft^2
Qg= Ug*A*∆T
= 0.152*22530*(98.6-75.2)
= 80134.704 Btu/hr

## Slide 13: HEAT GAIN THROUGH FRONT WALL(west)
(Front wall consisting of Entrance glass, Wall glass.)
Heat transfer through CONDUCTION
 | Type | Area(ft2) | U | CLTD | CLTDc | Q
Wall Glass | Reflective 6mm | 6012 | 0.83 | 14 | 19.6 | 97803.216
Entrance door glass | Single glazed | 600 | 0.88 | 14 | 19.6 | 10348.8

## Slide 14: HEAT GAIN THROUGH FRONT WALL(west)
Heat transfer through RADIATION
Qrad =A*SC*SCL (SCL= CLF x max SHGF)
SC = Shading coefficient
SCL= Solar cooling load factor = CLF x maximum SHGF
 | Area | SC | CLF | Max SHGF | SCL | Qrad
Wall Glass | 6012 | 0.27 | 0.82 | 196 | 160.72 | 260887.133
Entrance Glass | 600 | 0.57 | 0.82 | 196 | 160.72 | 54966.24

## Slide 15: Heat gained through Window, Exit door (East)
Conduction load
Radiation Load
 | Type/Numbers | Area | U | CLTD | CLTDc | Q
Window | Reflective/25 | 750 (3.75*8*25) | 0.83 | 14 | 19.6 | 12201.00
Exit Door | Single Glazed | 300 | 0.88 | 14 | 19.6 | 5174.4
 | Area | SC | CLF | MAX SHFG | SCL | Qrad
Window | 750 | 0.27 | 0.8 | 196 | 156.8 | 31752
Exit Door | 300 | 0.57 | 0.8 | 196 | 156.8 | 26812.8

## Slide 16
Heat gain through lights, peoples and electronic appliances
CALCULATION OF LIGHTENNG LOAD
Lightning Load(Ql) =Rule of Thumb(Watt/sq.ft)*Area(Sq.ft)*CLF
Assumptions: CLF=0.45 (Heavy weight simple furnishing )
LOAD THROUGH APPLIANCE
= RATING*CLF
CLF= 0.35
CALCULATION OF OCCUPANCY LOAD
Qs= No. of people*SHG*CLF
QL= No. of people*LHG

## Slide 18: Heat gain through lights, peoples and electronic appliances (Ground Floor)
Hall | No. of People | Activity type | SHG (Btu/hr) | LHG (Btu/hr) | Area of Lightening | Thumb rule | Appliances | Qapp (Btu/hr) | Numbers | Sensible Heat | Latent Heat
Yoga Hall | 50 | Heavy work | 580 | 870 | 4000 | 3 | - | - |  | 25990 | 43500
Photography Club | 10 | Office work | 250 | 200 | 625 | 2 | Laptops | 307 | 3 | 2659.85 | 2000
Dance Room | 20 | Heavy work | 580 | 870 | 2100 | 3 | Sound box | 650 | 1 | 11309.7 | 17400
Conference Room | 80 | Office work | 250 | 200 | 1050 | 2 | Laptops | 307 | 10 | 16219.5 | 16000

## Slide 19: Heat gain through lights, peoples and electronic appliances (First Floor)
HALL | No. of People | Activity type | SHG (Btu/hr) | LHG (Btu/hr) | Area of Lightening | Thumb rule | Appliances | Qapp (Btu/hr) | Numbers | Sensible Heat | Latent Heat
Movie Club | 10 | Light work | 250 | 200 | 1860 | 3 | Laptops | 307 | 2 | 4500.9 | 2000
Fine Art Club | 8 | Light work | 250 | 200 | 1380 | 3 | Laptops | 307 | 2 | 3497.9 | 1600
Xpression Hall | 30 | Light work | 250 | 200 | 3150 | 3 |  |  |  | 9577.5 | 6000
Robotics club | 15 | Light work | 250 | 200 | 725 | 3 | Laptops | 307 | 8 | 4500.85 | 3000
Aeromodelling club | 10 | Light work | 250 | 200 | 900 | 3 | Laptops | 307 | 5 | 3527.25 | 2000

## Slide 20: Calculation of infiltration load
QSensible= 1.08 * CFM * ΔT
QLatent= 4840 * CFM * Δw
Assumption : student activity center
10 CFM/person
From psychrometric chart indoor and outdoor conditions are as follows:-
= 0.0092 kg/kg of dry air
= 0.0321 kg/kg of dry air
Δw = 0.0229 kg/kg of dry air
= 98.6
= 75.2
= 23.4

## Slide 21: Calculation for infiltration & ventilation load
INFILTRATION
QSensible= 1.08 * CFM * ΔT*N where, N=No. Of people
= 1.08*10*23.4*223 Wc=0.0061 kg/kg of dry air
= 56356.56 Btu/hr
QLatent= 4840 * CFM * Δw*N
=4840*10* 0.0229 *223
= 247164.3 Btu/hr
VENTILATION
Qsensible = 1.08*CFM*ΔTc*N
= 1.08*10*54*223
= 130053.6 Btu/hr
Qlatent = 4840*Δwc*CFM*N
= 4840*0.026*10*223
= 280623.2 Btu/hr

## Slide 22: Calculation for total load
Total Sensible load
= Qspace +Qinfl +Qvent
= 1214113 Btu/hr
Total Latent load
= Qspace + Qinfl +Qvent
= 621287.5 Btu/hr
RSH= Qspace +Qinfl = 1084059.61 Btu/hr
RLH = Qspace + Qinfl = 340664.3 Btu/hr
Total Room Load = 1424723.91 Btu/hr =118.73 TR
SHF = = 0.761

## Slide 23
a
b
c
e
d
f

## Slide 24: Assumptions:- 20% fresh air used Coil temperature = 7 Air entering to the room = 15
From psychrometric chart
= 120 kj/kg
=47.5 kj/kg
bc = 0.2ab ( assumption 20% fresh air )
= 61 kj/kg
=26.6
Tcoil = 7ºC

## Slide 25: Temperature and enthalpy of various points
points | T º C | h (kj/kg)
a | 37 | 120
b | 24 | 48
c | 26.6 | 61
d | 11.6 | 31.9
e | 15 | 36
f | 7 | 23

## Slide 26
Bypass factor for cooling coil =
Bypass factor = 0.234
Fraction of fresh air = = = =0.2
Room load= (hb - he)
Mass flow rate of total air= 34.73 kg/sec
Mass flow rate of fresh air =6.945 kg/sec
Capacity of cooling coil= (hc - hd)
=1010.57 kw
= 287.91 TR
Capacity of heating coil= (he - hd)
= 142.38 KW

## Slide 27
Chart: Percentage of cooling load
| Walls | Windows | Roof | Floor | People+Appliances+Light | INFILTRATION | VENTILATION | Front Side Glass
 | 69943.82 | 141255.2 | 295895.502 | 80134.704 | 175283.45 | 303520.84 | 410676.8 | 358690.3488

## Slide 28
Thank You