## Sheet1
Given condition
Location: | Guwahati
type of building |  | Student activity center
Number of floor |  | 2
Floor Area |  | 22530
Floor to floor height |  | 11ft
building orientation:west facing
west side |  | reflective glasses
north & south |  | wall
east |  | window 18% area |  |  |  | wall 82% area
U factor
wall glass |  |  |  | 0.83
entrance & exit door glass |  |  |  | 0.88
north ,south & east wall |  |  |  | 0.1799
ground |  |  |  | 0.152
roof
window glass |  |  |  | 0.83
recommended ventilation |  |  |  | 10 CFM/ person
occupancy |  |  |  | 223 people
Design condition
Location: | (26.18'N,91.67'E)
Outdoor DBT |  |  |  |  | 98.6℉
Outdoor relative humidity |  |  |  |  | 80%
Indoor design DBT |  |  |  |  | 75.2 ℉
Indoor relative humidity |  |  |  |  | 50%
daily range |  |  |  |  | 21.5 ℉
wind velocity |  |  |  |  | 3.1 kmph
Calculation of CLTDc
CLTDc |  |  |  | = | CLTD +(78-inside design temp)+(mean outdoor temp-85)
mean outdoor temp |  |  |  | = | outdoor design DBT -(daily rangr/2)
mean outdoor temp |  |  |  | 87.8F
Walls |  |  |  | CLTD |  |  | CLTDc
north wall |  |  |  | 21 |  |  | 26.6
south wall |  |  |  | 26 |  |  | 31.6
east wall |  |  |  | 33 |  |  | 38.6
reflective glass |  |  |  | 14 |  |  | 19.6
window glass |  |  |  | 14 |  |  | 19.6
entrance door glass |  |  |  | 14 |  |  | 19.6
exit door glass |  |  |  | 14 |  |  | 19.6
[7 empty] | SENSIBLE HEAT GAIN THROUGH WALL | [7 empty] | Q=A*U*CLTDc
WALL |  |  | AREA ft^2 |  |  | U |  |  | CLTDc |  |  | SENSIBLE LOAD
reflective glass | glass (west) |  | 6012 |  |  | 0.83 |  |  | 19.6 |  |  | 97803.216
entrance door glass |  |  | 600 |  |  | 0.88 |  |  | 19.6 |  |  | 10348.8 |  |  |  | Qwall
north wall |  |  | 2490 |  |  | 0.1799 |  |  | 26.6 |  |  | 11915.4966 |  |  |  | 69943.8247
south wall |  |  | 2490 |  |  | 0.1799 |  |  | 31.6 |  |  | 14155.2516
east wall |  |  | 6318 |  |  | 0.1799 |  |  | 38.6 |  |  | 43873.0765 |  |  |  | Qwindow
Window glass(East) |  |  | 750 |  |  | 0.83 |  |  | 19.6 |  |  | 12201 |  |  |  | 141255.24
exit door glass |  |  | 300 |  |  | 0.88 |  |  | 19.6 |  |  | 5174.4
ground |  |  | 22530 |  |  | 0.152 |  |  | 23.4 |  |  | 80134.704 |  |  |  | Qfront
roof |  |  | 22530 |  |  | 0.2065 |  |  | 63.6 |  |  | 295895.502 |  |  |  | 358690.3488
[11 empty] | TOTAL | 571501.4467
[5 empty] | RADIATION HEAT LOAD CALCULATION | [7 empty] | Qrad=A*SC*SCL
SIDE |  | AREA ft^2 |  | shading coefficient |  |  | CLF |  | Max SHGF |  | SCL |  | Qradiation
reflective glass(West) |  | 6012 |  |  | 0.27 |  | 0.82 |  | 196 |  | 160.72 |  | 260887.1328
entrance door glass |  | 600 |  |  | 0.57 |  | 0.82 |  | 196 |  | 160.72 |  | 54966.24
window glass |  | 750 |  |  | 0.27 |  | 0.8 |  | 196 |  | 156.8 |  | 31752
exit door glass |  | 300 |  |  | 0.57 |  | 0.8 |  | 196 |  | 156.8 |  | 26812.8
[12 empty] | TOTAL | 374418.1728
[5 empty] | LOAD CALCULATION FOR GROUND FLOOR | [8 empty] | OCCUPANCY+LIGHT+APPLIANCES
HALL |  | NO.OF PEOPLE |  |  | SHG | CLF (shg) | LHG |  | AREA (light) |  | THUB RULE (w/ft^2) |  |  | CLF (light) |  | APPLIANCES | NO. | CLF(APPLI) | RATING | Qsensible | Qlatent
yoga hall |  | 50 |  |  | 580 | 0.71 | 870 |  | 4000 |  | 3 |  |  | 0.45 |  |  | 0 | 0 | 0 | 25990 | 43500
Dance hall |  | 20 |  |  | 580 | 0.71 | 870 |  | 2100 |  | 3 |  |  | 0.45 |  | sound system | 1 | 0.35 | 682 | 11309.7 | 17400
conference hall |  | 80 |  |  | 250 | 0.71 | 200 |  | 1050 |  | 2 |  |  | 0.45 |  | laptop | 10 | 0.35 | 307 | 16219.5 | 16000
photography club |  | 10 |  |  | 250 | 0.71 | 200 |  | 625 |  | 2 |  |  | 0.45 |  | laptop | 3 | 0.35 | 307 | 2659.85 | 2000
[5 empty] | LOAD CALCULATION FOR FIRST FLOOR | [8 empty] | OCCUPANCY+LIGHT+APPLIANCES
HALL |  | NO.OF PEOPLE |  |  | SHG | CLF (shg) | LHG |  | AREA (light) |  | THUB RULE (w/ft^2) |  |  | CLF (light) |  | APPLIANCES | NO. | CLF(APPLI) | RATING | Qsensible | Qlatent
Movie club |  | 10 |  |  | 250 | 0.71 | 200 |  | 1860 |  | 3 |  |  | 0.45 |  | laptops | 2 | 0.35 | 307 | 4500.9 | 2000
Fine art club |  | 8 |  |  | 250 | 0.71 | 200 |  | 1380 |  | 3 |  |  | 0.45 |  | Laptop | 2 | 0.35 | 307 | 3497.9 | 1600
Xpression hall |  | 30 |  |  | 250 | 0.71 | 200 |  | 3150 |  | 3 |  |  | 0.45 |  |  | 0 | 0.35 | 0 | 9577.5 | 6000
Aeromodelling club |  | 10 |  |  | 250 | 0.71 | 200 |  | 900 |  | 3 |  |  | 0.45 |  | laptops | 5 | 0.35 | 307 | 3527.25 | 2000
Robotics room |  | 15 |  |  | 250 | 0.71 | 200 |  | 725 |  | 3 |  |  | 0.45 |  | laptops | 8 | 0.35 | 307 | 4500.85 | 3000
[18 empty] | TOTAL |  | 81783.45 | 93500
INFILTRATION HEAT LOAD CALCULATION
Qappl+Qpeople
CFM | PEOPLE | To |  | Ti |  | ΔT |  | factor |  | Qsensible | [8 empty] | 175283.45
10 | 223 | 98.6 |  | 75.2 |  | 23.4 |  | 1.08 |  | 56356.56 |  | Qinf
CFM | PEOPLE | Wo |  | Wi |  | ΔW |  | factor |  | Qlatent |  | 303520.84
10 | 223 | 0.0321 |  | 0.0092 |  | 0.0229 |  | 4840 |  | 247164.28
VENTILATION HEAT LOAD CALCULATION
CFM | PEOPLE | To |  | Tc |  | ΔTc |  | factor |  | Qsensible
10 | 223 | 98.6 |  | 44.6 |  | 54 |  | 1.08 |  | 130053.6 |  | Qvant
CFM | PEOPLE | Wo |  | Wc |  | ΔWc |  | factor |  | Qlatent |  | 410676.8
10 | 223 | 0.0321 |  | 0.0061 |  | 0.026 |  | 4840 |  | 280623.2
|  |  |  | Qsensible total |  | 1214113.2295
|  |  |  | Qlatent total |  | 621287.48
|  |  |  | Qtotal |  | 1835400.6648
Cooling Load Components |  |  |  | Total Load (Btu/hr)
Walls |  |  |  | 69943.82
Windows |  |  |  | 141255.2
Roof |  |  |  | 295895.502
Floor |  |  |  | 80134.704
People+Appliances+Light |  |  |  | 175283.45
INFILTRATION |  |  |  | 303520.84
VENTILATION |  |  |  | 410676.8
Front Side Glass |  |  |  | 358690.3488
Qtotal |  |  |  | 1835400.6648